## line Assumption
line number | DISTANCES km | Type of line | Number of Conductors per Phase | Number of Circuits | Distance between phases (mm) | Distance between conductors(mm) | Voltage (kV) | Conductor type (Code number) | R conductor (ohm/ km) | R/n | Kg | RL | LL | CL | d mm | r mm
L12 | 120 | Single | 1 | 1 | 3350 | - | 220 | 315 | 0.0917 | 0.0917 | 0.811 | 0.0917 | 1.18 | 9.75 | 24.87 | 12.435
L23 | 90 | Single | 1 | 1 | 3350 | - | 220 | 315 | 0.0917 | 0.0917 | 0.811 | 0.0917 | 1.18 | 9.75 | 24.87 | 12.435
L34 | 60 | Double | 1 | 2 | 6000 | 3500 | 220 | 200 | 0.144 | 0.072 | 0.826 | 0.072 | 0.644 | 17.77 | 21 | 10.5
L45 | 50 | Double | 1 | 2 | 6000 | 3500 | 220 | 200 | 0.144 | 0.072 | 0.826 | 0.072 | 0.644 | 17.77 | 21 | 10.5
L56 | 80 | Double | 1 | 2 | 6000 | 3500 | 220 | 200 | 0.144 | 0.072 | 0.826 | 0.072 | 0.644 | 17.77 | 21 | 10.5
L67 | 110 | Double | 1 | 2 | 6000 | 3500 | 220 | 200 | 0.144 | 0.072 | 0.826 | 0.072 | 0.644 | 17.77 | 21 | 10.5
L78 | 250 | Bundle | 4 | 1 | 8000 | 300 | 220 | 4*200 | 0.144 | 0.036 | 0.826 | 0.036 | 0.863 | 13.023 | 21 | 10.5
L81 | 250 | Bundle | 4 | 1 | 8000 | 300 | 220 | 4*200 | 0.144 | 0.036 | 0.826 | 0.036 | 0.863 | 13.023 | 21 | 10.5
L13 | 160 | Double | 1 | 2 | 6000 | 3500 | 220 | 200 | 0.144 | 0.072 | 0.826 | 0.072 | 0.644 | 17.77 | 21 | 10.5
L15 | 180 | Double | 1 | 2 | 6000 | 3500 | 220 | 200 | 0.144 | 0.072 | 0.826 | 0.072 | 0.644 | 17.77 | 21 | 10.5
L35 | 160 | Double | 1 | 2 | 6000 | 3500 | 220 | 200 | 0.144 | 0.072 | 0.826 | 0.072 | 0.644 | 17.77 | 21 | 10.5
L46 | 150 | Single | 1 | 1 | 3400 | - | 220 | 315 | 0.0917 | 0.0917 | 0.811 | 0.0917 | 1.18 | 9.75 | 24.87 | 12.435
L57 | 100 | Double | 1 | 2 | 6000 | 3500 | 220 | 200 | 0.144 | 0.072 | 0.826 | 0.072 | 0.644 | 17.77 | 21 | 10.5
L58 | 220 | Bundle | 2 | 1 | 8000 | 300 | 220 | 2*450 | 0.062 | 0.031 | 0.809 | 0.031 | 1.0641 | 10.65 | 30.42 | 15.21
Caracas Area | 64749 Km^2
Vn kv | 220
Vb kv | 220
Sb MVA | 100
Wiring factor
# aluminum wires | # steel wires |  | kg
6 | 1 |  | 0,726
18 | 1 |  | 0,776
26 | 7 |  | 0,811
54 | 7 |  | 0,809
54 | 19 |  | 0,808
72 | 19 |  | 0,793

## Line parameters
line number | DISTANCES km | Type of line | Number of Conductors per Phase | Number of Circuits | Sb (MVA) | Voltage (kV) | Zb | Conductor type (Code number) | Diameter | kg | max Amp | Rcond | GMD | GMR | R | L (H/km) | XL (ohm/km) | C (nF/km) | Rt | XLt | XCt | r | x | b
L3 | 100 | Single | 1 |  | 100 | 400 | 1600 | 1250 | 47 | 0.793 | 1163 | 0.0231 | 10.0794 | 0.018635 | 0.0231 | 0.0012586 | 0.39541 | 9.1657 | 2.31 | 39.5412 | 287948.9477 | 0.0014437 | 0.024713 | 460718316.3524
L8 | 100 | Single | 1 |  | 100 | 400 | 1600 | 1250 | 47 | 0.793 | 1163 | 0.0231 | 10.0794 | 0.018635 | 0.0231 | 0.0012586 | 0.39541 | 9.1657 | 2.31 | 39.5412 | 287948.9477 | 0.0014437 | 0.024713 | 460718316.3524
L7 | 100 | Double | 2 |  | 100 | 400 | 1600 | 2*1250 | 47 | 0.793 | 2326 | 0.0231 | 7.674 | 0.44864 | 0.01155 | 0.00056787 | 0.1784 | 20.3993 | 1.155 | 17.8403 | 640863.6192 | 0.00072187 | 0.01115 | 1025381790.7598 | ror
L1 | 100 | Bundle | 6 |  | 100 | 400 | 1600 | 6*1250 | 47 | 0.793 | 6978 | 0.0231 | 10.0794 | 0.19066 | 0.00385 | 0.00079355 | 0.2493 | 13.6684 | 0.385 | 24.9302 | 429406.4674 | 0.00024062 | 0.015581 | 687050347.8401
L2 | 140 | Bundle | 4 |  | 100 | 400 | 1600 | 4*1250 | 47 | 0.793 | 4652 | 0.0231 | 10.0794 | 0.16333 | 0.005775 | 0.0008245 | 0.25902 | 13.6684 | 0.8085 | 36.2634 | 601169.0544 | 0.00050531 | 0.022665 | 961870486.9762
L4 | 200 | Bundle | 6 |  | 100 | 400 | 1600 | 6*1250 | 47 | 0.793 | 6978 | 0.0231 | 10.0794 | 0.19066 | 0.00385 | 0.00079355 | 0.2493 | 13.6684 | 0.77 | 49.8604 | 858812.9348 | 0.00048125 | 0.031163 | 1374100695.6802
L5 | 140 | Bundle | 6 |  | 100 | 400 | 1600 | 6*1250 | 47 | 0.793 | 6978 | 0.0231 | 10.0794 | 0.19066 | 0.00385 | 0.00079355 | 0.2493 | 13.6684 | 0.539 | 34.9023 | 601169.0544 | 0.00033687 | 0.021814 | 961870486.9762
L6 | 140 | Bundle | 6 |  | 100 | 400 | 1600 | 6*1250 | 47 | 0.793 | 6978 | 0.0231 | 10.0794 | 0.19066 | 0.00385 | 0.00079355 | 0.2493 | 13.6684 | 0.539 | 34.9023 | 601169.0544 | 0.00033687 | 0.021814 | 961870486.9762
DISTANCES
Single |  | Double |  |  |  | Double
d12 | 8 | d12 | 6.0208 | d1-1' | 13.4164 | dbundle (cm) | 30
d23 | 8 | d1'2 | 6.0208 | d2-2' | 7 | rbundle | 0.21213
d31 | 16 | d1'2' | 8.8459 | GMD12 | 7.2979 | d12 | 8
|  | d12' | 8.8459 | GMD23 | 7.2979 | d23 | 8
|  | d31 | 12 | GMD31 | 8.4853 | d31 | 16
|  | d3'1 | 6 | GMR1 | 0.50002 | Req | 0.17308 | 0.17308 | 0.17308 | 0.17308 | 0.17308
|  | d3'1' | 12 | GMR2 | 0.36118 | L58
|  | d31' | 6 | GMR3 | 0.50002 | d12 | 13
|  | Req1 | 0.5615 | Req | 0.5038 | d23 | 14.3265
|  | Req2 | 0.40559 |  |  | d31 | 9.6047
|  | Req3 | 0.5615 |  |  | rbundle | 0.15
[6 empty] | Req | #REF!

## Sheet1
line number | DISTANCES km | Type of line | Number of Conductors per Phase | Number of Circuits | Sb (MVA) | Voltage (kV) | Zb | Conductor type (Code number) | Diameter | kg | Rcond | GMD | GMR | R | L (H/km) | C (F/km) | Rt | XLt | XCt | r | x | b
Dam1 | 28.35 | Single | 1 | 1 | 100 | 400 | 1600 | 315 | 19.81 | 0.811 | 0.1444 | 10.0794 | 0.008033 | 0.1444 | 0.0014269 | 8.0222e-09 | 4.0937 | 12.7089 | 7.1449e-05 | 0.0025586 | 0.0079431 | 0.11432
Dam2 | 93.7 | Single | 1 | 1 | 100 | 400 | 1600 | 315 | 19.81 | 0.811 | 0.1444 | 10.0794 | 0.008033 | 0.1444 | 0.0014269 | 8.0222e-09 | 13.5303 | 42.0044 | 0.00023615 | 0.0084564 | 0.026253 | 0.37784
RoR | 38.81 | Double | 2 | 1 | 100 | 400 | 1600 | 250 | 22.16 | 0.811 | 0.1155 | 7.674 | 0.28695 | 0.05775 | 0.00065726 | 1.7462e-08 | 2.2413 | 8.0136 | 0.0002129 | 0.0014008 | 0.0050085 | 0.34065
Nuclear | 201.26 | Bundle | 4 | 1 | 100 | 400 | 1600 | 4*710 | 36.79 | 0.808 | 0.0407 | 10.0794 | 0.15435 | 0.010175 | 0.00083581 | 1.3466e-08 | 2.0478 | 52.8463 | 0.0008514 | 0.0012799 | 0.033029 | 1.3622
Wind | 52.87 | Bundle | 4 | 2 | 100 | 400 | 1600 | 4*1250 | 47 | 0.793 | 0.0231 | 10.0794 | 0.16333 | 0.005775 | 0.0008245 | 1.3466e-08 | 0.30532 | 13.6946 | 0.00022366 | 0.00019083 | 0.0085591 | 0.35785
Solar | 83.67 | Bundle | 4 | 3 | 100 | 400 | 1600 | 4*800 | 39.09 | 0.808 | 0.0362 | 10.0794 | 0.1567 | 0.00905 | 0.00083278 | 1.3466e-08 | 0.75721 | 21.8901 | 0.00035395 | 0.00047326 | 0.013681 | 0.56632
Gas | 26.07 | Bundle | 4 | 4 | 100 | 400 | 1600 | 4*1250 | 47 | 0.793 | 0.0231 | 10.0794 | 0.16333 | 0.005775 | 0.0008245 | 1.3668e-08 | 0.15055 | 6.7528 | 0.00011195 | 9.4096e-05 | 0.0042205 | 0.17911

## Questions
1) Demand to be satisfied In order to define it, consider following constraints/assumptions: a. Select one hour of the energy demand obtained in previous assignment. b. The energy demand for that hour will correspond to the power demand. c. The generation set point of each generator will correspond to the energy delivered for that hour (assuming that each power plant generates at constant power).
2) Define transmission power lines: In order to define it, consider following constraints/assumptions: a. Define the type of each of the power lines: single line, or double line, or bundle line (propose number of conductors per phase). There should be at least one of each type. b. Conductor arrangement, that is, distance between the conductors of the 3 phases and the bundle distance for one phase (if bundle line is choosen) for each of the power lines. Note: You can propose an arrangement or look for an existing one. c. Length of power line. The maximum length of transmission power line(s) will be 250 km.
3) Select conductor for the 3-phase AC transmission system: In order to define it, consider following constraints/assumptions: a. Select rated voltage level for transmission power lines. Note: You should chose 220 kV or 400 kV. b. Select ACSR conductors for the power lines from the table below. Note: You can chose a different conductor for each of the power lines. c. Calculate the electric parameters for each of the transmission power lines
4) Calculate the power of each power plant, the demand and the electric parameters of transmission power lines in p.u. For the calculation in p.u., consider Sb=100 MVA and Vb [kV] the rated voltage level consider for the transmission power lines
5) Represent the single-line scheme of the power system you are considering
6) Solve load flow with matpower (or similar software) a. Check voltages at the origin and at the end of each power line Note: normal values should be between 0,95 and 1,05 p.u. b. Check the currents through each power line Note: results should not surpass current rating of the conductors If in some case the current of a conductor of a power line is exceeded, select a new conductor with higher current rating and recalculate results.
7) OPTIONAL: Repeat the load flow for different hours and compare results.
8) Description of your team: organization and tasks

## G & D
Generator | Power rating (GWh)
Nuclear | 2.23
Wind | 0.2358
Solar | 4.3102
Hydro Dam | 1.29
Hydro Ran out | 1.2114
Gas | 2.4565
demand | 11.7339 | GWh